- Verify the water heater pressure relief valve and the drain valve, at the base of water heater are closed.

- Open the valve at the water meter with Black handle key.

- Open the main valve near the road with Blue handle 2" square key.

- Open the drain valve at north end of main walkway and let water run for 15-20 minutes to completely flush the main lines.

- Remove the planks blocking the restroom doors. Install inside each restroom, above the doors, for the summer.

- Close drain valve and open all faucets in clubhouse to flush lines and expel air.

- Close all faucets in the clubhouse and flush each toilet several times to check the toilet fill valves are working properly..

- Close all the drain valves at slips A30, A40, A50, B9, B19 and B29. Open water risers one at a time to expel air up and down the slips

- Close all faucets and valves and walk the docks listening for leaks. Check restrooms and kitchen area for sounds from leaks.

- Once the system has stabilized, with all faucets and drain valves closed, check the water meter for indication of leaks.

The flowmeter is a small red arrow which rotates as water flows through the valve and will indicate even small leakages.  Due to air in the water line, the red arrow may oscillate forwards and backwards slightly until pressures equalize.

Any consistent rotation in the forward direction means there is a leak somewhere in the system.

- Verify both ball valves on the north side of the sewage holding tank in the dry storage area are closed.

- Verify both ball valves in sewer line under the steps at the gangplank/ walkway are open.

- Verify the sewage pump out gate valve under the same steps is closed and cap on tight.

- Close the WATER HEATER, SEWER PUMP, and PUMP OUT PUMP circuit breakers.

- Use boat pump-out pump to fill sewage basin and let the sewage pump cycle several times to assure that fluid is reaching holding tank and there are no leaks in the system.

- Connect the pump-out hose and put the inlet in the lake to draw in lake water

- Set Clubhouse sewage pump switch to AUTO

- Select Pump-out pump switch to ON

When complete:

- Select pump-out pump switch to OFF

- Stow pump-out hose